## 1.1 Quantity of sludge
Table 1. The quantity of sludge
Value
Total solids in the influent sludge (kgTS/d) | 26319.501
Total solids concentration in the influent sludge (%) | 2.5
Sludge volumetric loading (m3/d) | 1032.1373
*Calculation of total solid
Suspended solid from primary settling | 18225 | kg/d | (From project work 2, section 4.4 Primary Settling)
Sludge from secondary settling | 2344.63 | kg/d | (From project work 2, section 4.6.2 Aerobic stage)
Qd | 90000 | m3/d | (Daily design flowrate in wastewater plant)
Molar mass of Fe3+ | 55.845 | g/mol
Molar mass of H2PO4- | 96.987 | g/mol
Molar mass of OH- | 17.008 | g/mol
Molar mass of P | 30.97 | g/mol
Influent P-tot | 6.58 | mg/L | (From project work 2, section 4.4 Primary Settling)
Effluent P-tot | 0.3 | mg/L | (From project work 2, section 4.8 Chemical precipitation of P)
Amount of P removed | 6.28 | mg/L
Based on the reaction
1 mol of P-removed will form 1 mol of precipitation
Mol of P-removed | 0.20278 | mol/m3
Mol of precipitation | 0.20278 | mol/m3
Mass of precipitation | 50.8908 | g/m3
Mass of precipitation per day | 4580171.2909 | g/d
| 4580.1713 | kg/d
Amount of reacting Fe | 0.32444 | mol/m3 | (This is the amount of Fe in the reaction
Fe3+ dosage | 24.91 | g/m3 | (From project work 2, section 4.8 Chemical precipitation of P. This is the amount of Fe that were added)
Mol of Fe3+ dosage | 0.44606 | mol/m3
Mol of Fe that are not reacted in P-removal | 0.12161 | mol/m3
The amount of Fe that are not reacted in P-removal will form Fe(OH)3. The mol of Fe(OH)3 will be equal to the mol of those Fe that are not reacted. Hence, the mass of Fe(OH)3 will be:
m_Fe(OH)3 | 12.9967 | g/m3
m_Fe(OH)3 per day | 1169699.7442 | g/d
| 1169.6997 | kg/d
The total amount of solid at this stage | 26319.501 | kg/d
Influent BOD | 255 | g/m3 | (From project 2, section 1.3 Quality and loading rate)
Effluent BOD | 10 | g/m3 | (From project 2, section 2 Discharge limit)
BOD removed | 245 | g/m3
BOD removed per day | 22050 | kg/d
Ratio of TS/BOD-removed | 1.1936 |  | (OK. This is in the typical range of 1-1.6 kgTS/kg BOD-removed)
Solid content | 2.5 | % | (Selecting from range 0.5-3% from the instruction)
Sludge density | 1.02 | kg/L
Amount of sludge | 1052780.0414 | kg/d
Sludge volumetric loading | 1032.1373 | m3/d

## 1.2 Sludge thickening
Table 2. Design parameter of thickener |  |  |  | Table 3. The mass balance of the thickener
| Value |  |  |  | Value
Solid loading rate in the thickener (kgTS/(m2*d)) | 40 |  |  | Solids in the effluent sludge (kgTS/d) | 12961.4014
Hydraulic loading rate in the thickener (m3/(m2*d)) | 8.1121 |  |  | Solid content in the effluent sludge (%) | 4
Number of thickeners | 2 |  |  | Effluent sludge flowrate (m3/d) | 317.6814
Surface area (m2) | 63.6173 |  |  | Reject water flowrate (m3/d) | 198.3872
Diameter (per thickener, m) | 9 |  |  | Reject water solids content (g/L) | 1
Depth of sludge (m) | 5 |  |  | Reject water solids loading (kg/d) | 198.3872
Volume (m3) | 318.0863
*Design of thickener
Solid loading rate | 40 | kgTS/(m2*d) | (Selecting from the range 40-80 kgTS/(m2*d) from the instruction)
Depth | 5 | m | Choosing from the range 3-5m as in the instruction)
Diameter | 9 | m | (Diameter is selected from value which are less than 10m)
Area | 63.6173 | m2
Volume | 318.0863 | m3
Influent flowrate | 516.0686 | m3/d | (The flowrate is divided by 2 so as to fulfill the requirement of hydraulic loading rate. This means there will be 2 thickener in the process)
Hydraulic loading | 8.1121 | m3/(m2*d) | (OK. In typical range of 6-12)
*Calculation of effluent sludge flowrate and reject water flowrate
TS, reject water | 1 | g/L
TS, sludge in | 0.025
TS, thickened sludge | 0.04
roo, sludge in | 1020 | kg/m3
roo, thickened sludge | 1020 | kg/m3
Q in | 516.0686 | m3/d
Mass solid 1 | 526390.0207 | kg/d
TS, 1 | 13159.7505 | kg/d
We have a mass balance equation
Q,1 = Q, reject + Q, thickened sludge => Q,reject = Q,1 - Q, thickened sludge = 516.07 - Q, thickened sludge
Solids are distributed between reject water and thickened sludge.
TS,1 = TS, reject + TS, thickened sludge
0.025 * 1020 kg/m3 * 516.07 m3/d = 1 kg/m3 * Q, reject m3/d + 0.04 * 1020 kg/m3 * Q, thickened sludge m3/d
0.025 * 1020 * 516.07 = 1 * (516.07 - Q, thickened sludge) + 0.04 * 1020 * Q, thickened sludge
13159.79 = 516.07 - Q,thickened sludge + 40.8 * Q, thickened sludge
12643. 72 =39.8 * Q, thickened sludge
Q, thickened sludge | 317.6814 | m3/d
Q, reject | 198.3872 | m3/d
TS, thickened sludge | 12961.4014 | kg/d
TS, reject | 198.3872 | kg/d | (This is calculated by Q, reject * TS, reject = Q, reject * 1 = Q, reject)
Total | 13159.7886 | kg/d
Sludge to thickening:
Q = 516.07 m3/d
roo = 1020 kg/m3
TS = 2,5 m-%
Gravity thickener
Thickened sludge
roo = 1020 kg/m3
TS = 4 m-%
Reject water
TS = 1 g/L = 1 kg/m3

## 1.3 Stabilization by anaerobic
Table 4. The input values to design anaerobic digestion |  |  |  | Table 5. The design parameters of anaerobic digestion
| Value |  |  |  | Value
Temperature (oC) | 35 |  |  | Sludge retention time (d) | 20.2991
Influent bCOD (g/m3) | 6000 |  |  | Volume of reactor (m3) | 6448.661
Effluent bCOD (g/m3) | 600 |  |  | Px (kg/d) | 85.2956
Safety factor | 5 |  |  | Methane production (m3/d) | 556.6559
Y | 0.08 |  |  | Km driven with biogas produced (km) | 46543.1344
K_s | 160
μ_m | 0.35
k_d | 0.03
* Selection of input value to design anaerobic digestion
Y | 0.08 | g VSS/g COD | (Solid yields, from table 27-13 Davis 2010)
K_s | 160 | mg/L | (Half velocity constant, from table 27-13 Davis 2010)
μ_m | 0.35 | g/(g*d) | (Max specific growth rate, table 27-13 Davis 2010)
k_d | 0.03 | g/(g*d) | (Decay coefficient, table 27-13 Davis 2010)
bCOD_influent | 6000 | g/m3
bCOD_effluent | 600 | g/m3
By using equation 27-23 in Davis 2010, the solid retention time (SRT) is calculated
1/θc | 0.24632 | d^-1 | (Equation 27-23 in Davis 2010)
θc | 4.0598 | d
θc (with safety factor) | 20.2991 | d | (Assuming safety factor = 5 as in example 27-6 in Davis 2010)
By comparing the SRT with table 18-15 for the requirement of process to significantly reduce pathogens (PSRP), we
could see that the SRT exceeds the PSRP as typical value for SRT at 35oC is 15 days.
Q_sludge in | 317.6814 | m3/d | (This is the amount of sludge after thickening and from 1 thickener)
Volume of digester | 6448.661 | m3 | (V = Q*t. This is volume of 1 digester)
* Estimating the mass of biological solids synthesized
Y_obs | 0.049721 | kg MLVSS/kg BOD5 removed | (Observed yield, equation 23-37 Davis 2010)
Px | 85.2956 | kg/d | (Equation 23-38, net waste activated sludge produced each day in terms of VSS)
* Estimating methane production
CH4 equivalent of COD converted | 0.35022 | L/g COD | (Equation 27-22 in Davis 2010. This is the amount of CH4 equivalent of COD converted under anaerobic condition)
Actual gas production | 0.39509 | L CH4/g COD | (Based on equation 27-24 in Davis 2010)
Methane production | 556.6559 | m3/d
Biogas production | 856.3937 | m3/d | (As in the instruction the biogas contain 65% of CH4)
Total biogas production | 1712.7873 | m3/d | (This is total amount of biogas produced from 2 digesters in this project work)
Consumption of 1 vehicle | 0.046 | kg biogas/km | (As in the instruction, 1 vehicle consumes 4.6 kg biogas/100 km)
Biogas density | 1.25 | kg/m3 | (Source: Teferra, D. M., Wubu, W. (2018). Biogas for Clean Energy. IntechOpen. DOI: 10.5772/intechopen.79534)
Amount of biogas | 2140.9842 | kg/d
Amount of km that a vehicle can travel | 46543.1344 | km/d